| BR 082 085 | ClassicLine body safety shower, wall mounted, exposed pipework |
| --- | --- |
| ClassicLine body safety shower, wall mounted, exposed pipework - wall flange with 4 mounting holes of stainless steel, chemical resistant green powder coated, water connection 3/4“ female - connection piece made of stainless steel, for quick on-site installation and easy alignment of the shower arm - ball valve ¾” made of dezincification-resistant brass, with quick connect system, pull rod actuation, DIN-DVGW tested and certificated - pull rod with ring handle of stainless steel, chemical resistant green powder coated, length 700 mm - wall shower arm ¾“ of stainless steel, chemical resistant green powder coated, projection 630 mm - integrated automatic flow regulator 50 litres / minute for a standard-compliant spray pattern at a specified working range of 1.5 to 3 bar flow pressure - high-performance shower head of chemical resistant plastics, black, with improved spray pattern, corrosion resistant, largely calcification- and maintenance-free, very robust, self-draining - sign for body safety shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 metre - mounting height 2345 mm (± 100 mm) - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717 - according to ANSI Z358.1-2014, EN 15154-1:2006 and EN 15154-5:2019 - DIN-DVGW tested and certificated Manufacturer: B-SAFETY or equal Article-No.: BR 082 085 Technical Specifications Minimum flow pressure: 1.5 bar Operating pressure: 1.5 to 3 bar Flow rate: 50 l/min Water inlet: ¾“ female Product overview BR 082 085: flow rate 50 l/min (hazard class I according to EN 15154-5:2019) BR 082 085 / 75L: flow rate 75 l/min / 20 GPM (hazard class II according to EN 15154-5:2019) BR 082 085 / 110L: flow rate 110 l/min (hazard class III according to EN 15154-5:2019) |  |