| BR 073 095 | PremiumLine safety shower arm, ceiling mounted, exposed pipework |
| --- | --- |
| PremiumLine safety shower arm, ceiling mounted, exposed pipework - ceiling flange with 4 mounting holes of stainless steel, polished, water inlet ¾” female - ceiling shower arm ¾“ made of stainless steel, polished, headroom 600 mm - integrated automatic flow regulation 50 l/min. for a spray pattern acc. to the norms at a specified operating range of 1.5 to 3 bar dynamic water pressure - high-performance shower head of stainless steel, polished, with improved spray pattern, corrosion resistant, largely scale and maintenance-free, very robust, self-draining - sign for body safety shower according to DIN EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 metre - mounting height 2800 mm (± 100 mm) - according to BGI/GUV-I 850-0, DIN 1988 and DIN EN 1717 - according to ANSI Z358.1-2014, DIN EN 15154-1:2006 and DIN EN 15154-5:2019 - DIN-DVGW tested and certificated Manufacturer: B-SAFETY or equal Article-No.: BR 073 095 Technical Specifications Minimum flow pressure: 1.5 bar Operating pressure: 1.5 to 3 bar Flow rate: 50 l/min Water inlet: ¾“ female # Mounting-Instructions For an installation in accordance with DIN EN 15154-1:2006 it must be ensured, that the safety shower installation is self-draining between valve and shower head. Product overview BR 073 095: flow rate 50 l/min (hazard class I according to DIN EN 15154-5:2019) BR 073 095 / 75L: flow rate 75 l/min / 20 GPM (hazard class II according to DIN EN 15154-5:2019) BR 073 095 / 110L: flow rate 110 l/min (hazard class III according to DIN EN 15154-5:2019) |  |