| BR 868 085 | ClassicLine safety shower combination, with eye-/face wash unit with bowl and lid, wall mounted, exposed pipework |
| --- | --- |
| ClassicLine safety shower combination, with eye-/face wash unit with bowl and lid, wall mounted, exposed pipework - including top and bottom water inlet ¾” female for installation in circulation lines, plug ¾” of stainless steel - wall flange with 4 mounting holes of stainless steel, chemical resistant green powder coated, water inlet ¾” female - connection piece of stainless steel, for easy installation and alignment of the shower - ball valve ¾” made of dezincification-resistant brass, with quick connect system and pull rod actuation, DIN-DVGW tested and certificated - pull rod with ring handle of stainless steel, chemical resistant green powder coated, length 700 mm - wall shower arm ¾“ of stainless steel, chemical resistant green powder coated, projection 630 mm - integrated automatic flow regulation 50 l/min. for a spray pattern acc. to the norms at a specified operating range of 1.5 to 3 bar dynamic water pressure - high-performance shower head of chemical resistant plastics, black, with improved spray pattern, corrosion resistant, largely calcification- and maintenance-free very robust, self-draining - sign for body safety shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 metre - two connection pipes ¾“ of stainless steel, chemical resistant green powder coated, total length 1500 mm - wall flange with 4 mounting holes of stainless steel, chemical resistant green powder coated, water inlet ¾” female - integrated PremiumLine eye-/face wash unit with bowl and lid, wall mounted - housing, lid and bowl made of UV and impact resistant ABS plastics, water outlet 1 ½“ male - integrated protective cover against dust - actuation by pulling down the lid - ball valve 3/8“ of brass, with lever actuation by lid, DIN-DVGW tested and certificated - aerators made of brass with a very limited spray pattern, chrome-plated - with integrated flow regulation valve 3/8” for setting the desired spray height and flow rate, water inlet 3/8” male - inclusive sign for eye shower according to EN ISO 7010 und ASR A1.3 on the lid, dimensions 170 x 170 mm, viewing distance 17 metre - mounting height 810 mm (± 100 mm) - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717 - according to ANSI Z358.1-2014, EN 15154-1:2006, EN 15154-2:2006 and EN 15154-5:2019 - DIN-DVGW tested and certificated Manufacturer: B-SAFETY or equal Article-No.: BR 868 085 Technical Specifications Minimum flow pressure: 1.5 bar Operating pressure: 1.5 to 3 bar Flow rate body shower: 50 l/min Flow rate eye shower: 14 l/min Water inlet: ¾“ female Product overview BR 868 085: flow rate 50 l/min (hazard class I according to EN 15154-5:2019) BR 868 085 / 75L: flow rate 75 l/min / 20 GPM (hazard class II according to EN 15154-5:2019) BR 868 085 / 110L: flow rate 110 l/min (hazard class III according to EN 15154-5:2019) |  |