| BR 305 195 | PremiumLine self-draining eye shower with stainless steel bowl, floor mounted |
| --- | --- |
| B-SAFETY PremiumLine self-draining eye shower with stainless steel bowl, floor mounted - base plate with 4 mounting holes of stainless steel, polished, dimensions 200 x 200 mm - stand pipe 1 ¼” of stainless steel, polished, with top and bottom water inlet 1 ¼” female, total height 1025 mm - ball valve 1” of stainless steel, foot lever actuation of stainless steel, inclusive self-draining to the upper edge of the ball valve near the bottom, water inlet 1” male, DIN-DVGW tested and certificated - foot lever in the shape of a T of stainless steel profile, covered with black non-slip tape, total width 350 mm - connection pipe of stainless steel for easy installation and alignment of the shower, polished - integrated flow regulation 14 litre / minute for a standard-compliant jet pattern at a specified working range of 2.5 to 5 bar flow pressure - high-performance spray heads made of stainless steel for large-scale dispersion of water, with plastic spray plate, largely free of calcification, with rubber sleeves and sealed dust caps with folding mechanism, mounted over distributor fork - bowl made of stainless steel, diameter 275 mm, polished, water outlet 1 ¼” male - sign for eye shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 100 x 100 mm, viewing distance 10 metre - total height 1025 mm, projection 345 mm, total width incl. lever 425 mm - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717 - according to ANSI Z358.1-2014 and EN 15154-2:2006 - DIN-DVGW tested and certificated Manufacturer: B-SAFETY or equal Article-No.: BR 305 195 Technical Specifications Minimum flow pressure: 2.5 bar Operating pressure: 2.5 to 5 bar Flow rate: 14 l/min Water inlet: 1” male Water outlet: 1 1/4” male |  |