| BR 832 195 | PremiumLine self-draining body safety shower with eye shower, floor mounted |
| --- | --- |
| B-SAFETY PremiumLine self-draining body safety shower with eye shower, floor mounted - base plate with 4 mounting holes of stainless steel, polished, dimensions 200 x 200 mm - stand pipe 1 ¼” of stainless steel three-part, polished, total height 2330 mm - ball valve 1” of stainless steel, foot lever actuation of stainless steel, inclusive self-draining to the upper edge of the ball valve near the bottom, water inlet 1” male, DIN-DVGW tested and certificated - foot lever in the shape of a T of stainless steel profile, covered with black non-slip tape, total width 350 mm - wall shower arm ¾“ of stainless steel, polished, projection 600 mm - integrated automatic flow regulation 50 l/min. for a spray pattern acc. to the norms at a specified operating range of 1.5 to 3 bar dynamic water pressure - high-performance shower head of stainless steel, polished, with improved spray pattern, corrosion resistant, largely calcification- and maintenance-free, very robust, self-draining - sign for body safety shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 metre - integrated PremiumLine safety eye shower with two spray heads 45°, mounting height 970 mm, orientation of eye shower freely selectable on site - connection pipe of stainless steel for easy installation and alignment of the shower, polished, water inlet ¾” male - ball valve ½” of stainless steel, with lever actuation, DIN-DVGW tested and certificated, including self-draining to the upper edge of the ball valve near the bottom - operating lever of stainless steel, polished, with large arrow in application direction - high-performance spray heads made of stainless steel for large-scale dispersion of water, with plastic spray plate, largely free of calcification, with rubber sleeves and sealed dust caps with folding mechanism, mounted over distributor fork - integrated flow regulation 14 litre / minute for a standard-compliant jet pattern at a specified working range of 1.5 to 5 bar flow pressure - sign for eye shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 100 x 100 mm, viewing distance 10 metre - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717 - according to ANSI Z358.1-2014, EN 15154-1:2006, EN 15154-2:2006 and EN 15154-5:2019 - DIN-DVGW tested and certificated Manufacturer: B-SAFETY or equal Article-No.: BR 832 195 Technical Specifications Minimum flow pressure: 1.5 bar Operating pressure: 1.5 to 3 bar Flow rate body shower: 50 l/min Flow rate eye shower: 14 l/min Water inlet: 1” male Product overview BR 832 195: flow rate 50 l/min (hazard class I according to EN 15154-5:2019) BR 832 195 / 75L: flow rate 75 l/min / 20 GPM (hazard class II according to EN 15154-5:2019) BR 832 195 / 110L: flow rate 110 l/min (hazard class III according to EN 15154-5:2019) |  |