| BR 885 095 | PremiumLine frost-protected self-draining body safety shower, actuation by 3-way ball valve, wall mounted |
| --- | --- |
| PremiumLine frost-protected self-draining body safety shower, actuation by 3-way ball valve, wall mounted - 3-way-ball-valve ¾” of brass that automatically drains the shower downwards when not in use, water inlet ¾” female - spindle extension, standard length 800 mm, can be shortened to the appropriate length on site, including stainless steel push rosette to cover the installation - adjustable plastic clamp-lever-handle, lockable with tools, orange, total length 110 mm - actuation via swivelling lever, opening angle 90°, not self-closing - wall shower arm ¾“ of stainless steel, polished, projection 470 mm - integrated automatic flow regulation 50 l/min. for a spray pattern acc. to the norms at a specified operating range of 1.5 to 3 bar dynamic water pressure - high-performance shower head of stainless steel, polished, with improved spray pattern, corrosion resistant, largely calcification- and maintenance-free, very robust, self-draining - push-on rosette of stainless steel to cover the installation - sign for body safety shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 metre - information sign "OPEN" for confusion-free use in an emergency, orange, photoluminescent according to DIN 67510 - mounting height 2345 mm (± 100 mm) - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717 - according to ANSI Z358.1-2014, EN 15154-1:2006 and EN 15154-5:2019 Manufacturer: B-SAFETY or equal Article-No.: BR 885 095 Technical Specifications Minimum flow pressure: 1.5 bar Operating pressure: 1.5 to 3 bar Flow rate: 50 l/min Water inlet: ¾“ female Product overview BR 885 095: flow rate 50 l/min (hazard class I according to EN 15154-5:2019) BR 885 095 / 75L: flow rate 75 l/min / 20 GPM (hazard class II according to EN 15154-5:2019) BR 885 095 / 110L: flow rate 110 l/min (hazard class III according to EN 15154-5:2019) |  |