| BR 250 085 | ClassicLine safety eye shower with two spray heads 45°, wall mounted, exposed pipework |
| --- | --- |
| ClassicLine safety eye shower with two spray heads 45°, wall mounted, exposed pipework - wall flange with 4 mounting holes made of stainless steel, chemical resistant green powder coated, water inlet ¾” female - connection pipe of stainless steel for easy installation and alignment of the shower, chemical resistant green powder coated - ball valve ½” of stainless steel, with PUSH-lever actuation, DIN-DVGW tested and certificated - big push plate made of steel, chemical resistant green powder coated, length 130 mm, with large signal "PUSH", luminescent according to DIN 67510 - integrated flow regulation 14 litre / minute for a standard-compliant jet pattern at a specified working range of 1.5 to 5 bar flow pressure - high-performance spray heads for large-scale dispersion of water, 45° angled, with plastic spray plate, low calcification, incl. rubber sleeves and sealed dust caps, mounted over distributor fork - sign for eye shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 100 x 100 mm, viewing distance 10 metre - height 200 mm, projection 310 mm, total width incl. lever 250 mm - mounting height 900 mm (± 200 mm) - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717 - according to ANSI Z358.1-2014 and EN 15154-2:2006 - DIN-DVGW tested and certificated Manufacturer: B-SAFETY or equal Article-No.: BR 250 085 Technical Specifications Minimum flow pressure: 1.5 bar Operating pressure: 1.5 to 5 bar Flow rate: 14 l/min Water inlet: ¾“ female |  |