| BR 880 095 | PremiumLine frost-protected self-draining eye shower, actuation by 3-way ball valve, wall mounted |
| --- | --- |
| PremiumLine frost-protected self-draining eye shower, actuation by 3-way ball valve, wall mounted - 3-way-ball-valve ¾” of brass that automatically drains the shower downwards when not in use, water inlet ¾” female - spindle extension, standard length 800 mm, can be shortened to the appropriate length on site, including stainless steel push rosette to cover the installation - adjustable plastic clamp-lever-handle, lockable with tools, orange, total length 110 mm - actuation via swivelling lever, opening angle 90°, not self-closing - connection pipe of stainless steel, polished, length 120 mm, water inlet ¾” female, from behind through the wall - integrated flow regulation 14 litre / minute for a standard-compliant jet pattern at a specified working range of 1.5 to 5 bar flow pressure - high-performance spray heads for large-scale dispersion of water of stainless steel, polished, 45° angled, with plastic spray plate, low calcification, incl. rubber sleeves and sealed dust caps, mounted over distributor fork - push-on rosette of stainless steel to cover the installation - sign for eye shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 100 x 100 mm, viewing distance 10 metre - information sign "OPEN" for confusion-free use in an emergency, orange, photoluminescent according to DIN 67510 - mounting height 900 mm (± 200 mm) - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717 - according to ANSI Z358.1-2014 and EN 15154-2:2006 Manufacturer: B-SAFETY or equal Article-No.: BR 880 095 Technical Specifications Minimum flow pressure: 1.5 bar Operating pressure: 1.5 to 5 bar Flow rate: 14 l/min Water inlet: ¾“ female |  |