| BR 089 085 / V | ClassicLine variable body safety shower, for installation in suspended ceilings |
| --- | --- |
| ClassicLine variable body safety shower, for installation in suspended ceilings - connection adapter of stainless steel, polished, with integrated automatic flow regulation 50 l/min. for a spray pattern acc. to the norms at a specified operating range of 1.5 to 3 bar dynamic water pressure, water inlet ¾” female - ball valve ¾” made of dezincification-resistant brass, with pull rod actuation, DIN-DVGW tested and certificated - pull rod with ball handle of stainless steel, length variable (min. 710 mm - max. 2040 mm) - slotted stainless steel rosette for passage through the suspended ceiling - double nipple ¾” of stainless steel - ceiling flange with 4 mounting holes of stainless steel, chemical resistant green powder coated - connection pipe ¾“ of stainless steel, chemical resistant green powder coated, length variable according to specification (total width min. 285 mm - max. 1535 mm) - ceiling flange with 4 mounting holes of stainless steel, chemical resistant green powder coated - connection pipe ¾“ of stainless steel, chemical resistant green powder coated, headroom variable according to specification (min. 360 mm - max. 1610 mm) - high-performance shower head of chemical resistant plastics, black, with improved spray pattern, corrosion resistant, largely scale and maintenance-free, very robust, self-draining - round rosette of stainless steel for installation of the shower head in the suspended ceiling - sign for body safety shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 metre - mounting height according to the standards listed below: lower edge of high-performance shower head 2200 mm (± 100 mm) height above floor level - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717 - according to ANSI Z358.1-2014, EN 15154-2:2006 and EN 15154-5:2019 - DIN-DVGW tested and certificated Manufacturer: B-SAFETY or equal Article-No.: BR 089 085 / V Technical Specifications Minimum flow pressure: 1.5 bar Operating pressure: 1.5 to 3 bar Flow rate: 50 l/min Water inlet: ¾“ female Product overview BR 089 085 / V: flow rate 50 l/min (hazard class I according to EN 15154-5:2019) BR 089 085 / V75L: flow rate 75 l/min / 20 GPM (hazard class II according to EN 15154-5:2019) BR 089 085 / V110L: flow rate 110 l/min (hazard class III according to EN 15154-5:2019) |  |