| BR 083 095 / V | PremiumLine variable body safety shower, ceiling mounted |
| --- | --- |
| PremiumLine variable body safety shower, ceiling mounted - connection pipe ¾“ of stainless steel, polished, length 75 mm, water inlet ¾” male - push-on rosette of polyamide to cover the installation - ball valve ¾” of stainless steel, with pull rod actuation, DIN-DVGW tested and certificated - pull rod with ring handle of stainless steel, polished, length variable (min. 860 mm - max. 1660 mm) - ceiling shower arm ¾“ of stainless steel, polished, headroom variable according to specification (min. 425 mm - max. 1225 mm) - integrated automatic flow regulation 50 l/min. for a spray pattern acc. to the norms at a specified operating range of 1.5 to 3 bar dynamic water pressure - high-performance shower head of stainless steel, polished, with improved spray pattern, corrosion resistant, largely calcification- and maintenance-free, very robust, self-draining - sign for body safety shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 metre - mounting height according to the standards listed below: lower edge of high-performance shower head 2200 mm (± 100 mm) height above floor level - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717 - according to ANSI Z358.1-2014, EN 15154-1:2006 and EN 15154-5:2019 - DIN-DVGW tested and certificated Manufacturer: B-SAFETY or equal Article-No.: BR 083 095 / V Technical Specifications Minimum flow pressure: 1.5 bar Operating pressure: 1.5 to 3 bar Flow rate: 50 l/min Water inlet: ¾“ male Product overview BR 083 095 / V: flow rate 50 l/min (hazard class I according to EN 15154-5:2019) BR 083 095 / V75L: flow rate 75 l/min / 20 GPM (hazard class II according to EN 15154-5:2019) BR 083 095 / V110L: flow rate 110 l/min (hazard class III according to EN 15154-5:2019) |  |