| BR 023 995 | PremiumLine safety shower valve with draining, wall mounted recessed version |
| --- | --- |
| PremiumLine safety shower valve with draining, wall mounted recessed version - cover plate made of stainless steel, with 4x fixing holes (diameter 4.50 mm) in the corners. - ball valve made of stainless steel, DIN-DVGW tested and approved - including 2x stainless steel union pipe fittings for simplified on-site installation, water inlet ¾” female - flow rate min. 60 litres / minute at 1 bar flow pressure - adjustable plastic clamp-lever-handle, lockable with tools, orange, total length 110 mm - actuation via swivelling lever, opening angle 90°, not self-closing - integrated draining valve for automatic or manual emptying - information sign "OPEN" for confusion-free use in an emergency, orange, photoluminescent according to DIN 67510 - mounting height for levers according to the standards mentioned below: 0 to 1750 mm height above floor level - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717 - according to ANSI Z358.1-2014, EN 15154-1:2006 and EN 15154-5:2019 Manufacturer: B-SAFETY or equal Article-No.: BR 027 995 Technical Specifications Minimum flow pressure: 1 bar Operating pressure: 1 to 5 bar Flow rate: at least 60 l/min at 1 bar flow pressure Water inlet: ¾“ female # Mounting-Instructions For an installation in accordance with EN 15154-1:2006 it must be ensured, that the safety shower installation is self-draining between valve and shower head. |  |