| BR 028 995 | PremiumLine safety shower valve in stainless steel cabinet, with draining, wall mounted, recessed version |
| --- | --- |
| PremiumLine safety shower valve in stainless steel cabinet, with automatic draining, wall mounted, recessed version - recessed stainless steel cabinet, cover for maintenance work removable, dimensions (H x W): 400 x 300 mm, installation dimensions (H x W x D): 350 x 251 x 62 mm - ball valve ¾“ of stainless steel, with lever actuation, DIN-DVGW tested and certificated - including 2x stainless steel union pipe fittings for simplified on-site installation, water inlet ¾” female - flow rate at least 60 l/min at 1 bar flow pressure - actuation via lever made of stainless steel, polished, length 160 mm, opening angle 90°, not self-closing - robust handle of plastics, black, diameter 25 mm, length 90 mm - integrated drain valve with automatic or manual drain, mounted on the outside of the lid - information sign "OPEN" for confusion-free use in an emergency, orange, photoluminescent according to DIN 67510 - mounting height for lever according to the standards listed below: 0 to 1750 mm height above floor - according to BGI/GUV-I 850-0, DIN 1988 and DIN EN 1717 - according to ANSI Z358.1-2014, DIN EN 15154-1:2006 and DIN EN 15154-5:2019 Manufacturer: B-SAFETY or equal Article-No.: BR 028 995 Technical Specifications Minimum flow pressure: 1 bar Operating pressure: 1 to 5 bar Flow rate: at least 60 l/min at 1 bar flow pressure Water inlet: ¾“ female # Mounting-Instructions For an installation in accordance with DIN EN 15154-1:2006 it must be ensured, that the safety shower installation is self-draining between valve and shower head. |  |