| BR 022 995 | PremiumLine rod operated safety shower valve, wall mounted, exposed pipework |
| --- | --- |
| PremiumLine rod operated safety shower valve, wall mounted, exposed pipework - ball valve with pull rod actuation on wall flange of stainless steel, can be mounted either on the right or left side of the door, DIN-DVGW tested and certificated, water inlet ¾” female - flow rate at least 60 l/min at 1 bar flow pressure - pull rod with ring handle made of stainless steel, polished, length 700 mm - holder for pull rod made of stainless steel, polished - opening angle 90°, not self-closing - information sign "OPEN" for confusion-free use in an emergency, orange, photoluminescent according to DIN 67510 - mounting height for lower edge of pull rod handle according to the standards listed below: 0 to 1750 mm height above floor - according to BGI/GUV-I 850-0, DIN 1988 and DIN EN 1717 - according to ANSI Z358.1-2014, DIN EN 15154-1:2006 and DIN EN 15154-5:2019 Manufacturer: B-SAFETY or equal Article-No.: BR 022 995 Technical Specifications Minimum flow pressure: 1 bar Operating pressure: 1 to 5 bar Flow rate: at least 60 l/min at 1 bar flow pressure Water inlet: ¾“ female # Mounting-Instructions For an installation in accordance with DIN EN 15154-1:2006 it must be ensured, that the safety shower installation is self-draining between valve and shower head. |  |