| BR 834 085 | ClassicLine body safety shower with hand-held eye shower with two spray heads 45°, floor mounted |
| --- | --- |
| ClassicLine body safety shower with hand-held eye shower with two spray heads 45°, floor mounted - including top and bottom water inlet 1 ¼” female for installation in circulation lines, plug 1 ¼” of stainless steel - base plate with 4 mounting holes of stainless steel, chemical resistant green powder coated, diameter 200 mm - stand pipe 1 ¼” of stainless steel three-part, chemical resistant green powder coated, with top and bottom water inlet 1 ¼” female, total height 2300 mm - connection piece of stainless steel, for easy installation and alignment of the shower - ball valve ¾” made of dezincification-resistant brass, with quick connect system and pull rod actuation, DIN-DVGW tested and certificated - pull rod with ring handle of stainless steel, chemical resistant green powder coated, length 700 mm - wall shower arm ¾“ of stainless steel, chemical resistant green powder coated, projection 630 mm - integrated automatic flow regulation 50 l/min. for a spray pattern acc. to the norms at a specified operating range of 1.5 to 3 bar dynamic water pressure - high-performance shower head of chemical resistant plastics, black, with improved spray pattern, corrosion resistant, largely scale and maintenance-free, very robust, self-draining - sign for body safety shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 metre - inclusive ClassicLine hand-held eye shower with two spray heads 45°, for mounting on standpipe, position and orientation freely selectable - ergonomically shaped handle with integrated, adjusting activation made of plastics, valve not self-closing - high-performance spray heads for large-scale dispersion of water, 45° angled, with plastic spray plate, largely free of calcification, with rubber sleeves and sealed dust caps - integrated flow regulation 14 litre / minute for a standard-compliant jet pattern at a specified working range of 2 to 5 bar flow pressure - integrated backflow preventer to protect the drinking water - stainless steel covered hose, length 1.5 meter, water inlet ½” female, DIN-DVGW tested and certificated - sturdy wall bracket with positioning of the shower, including mounting kit for mounting on the standpipe - sign for eye shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 100 x 100 mm, viewing distance 10 metre - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717 - according to ANSI Z358.1-2014, EN 15154-1:20006, EN 15154-2:2006 and EN 15154-5:2019 - DIN-DVGW tested and certificated Manufacturer: B-SAFETY or equal Article-No.: BR 834 085 Technical Specifications Minimum flow pressure: 1.5 bar Operating pressure: 1.5 to 3 bar Flow rate body shower: 50 l/min Flow rate eye shower: 14 l/min Water inlet: 1 ¼” female Dimensions (H x W x D): 2300 x 200 x 630 mm Product overview BR 834 085: flow rate 50 l/min (hazard class I according to EN 15154-5:2019) BR 834 085 / 75L: flow rate 75 l/min / 20 GPM (hazard class II according to EN 15154-5:2019) BR 834 085 / 110L: flow rate 110 l/min (hazard class III according to EN 15154-5:2019) |  |