| BR 888 395 | PremiumLine frostprotected self-draining safety shower station with surrounding protection cage, with underfloor actuation |
| --- | --- |
| PremiumLine frostprotected self-draining safety shower station with surrounding protection cage, with underfloor actuation - frame made of stainless steel tubes, dimensions (H x W x D): 960 x 850 x 900 mm - platform actuation for safety shower made of galvanized steel, mounted with chain on angle diversion, dimensions (W x D): 800 x 800 mm - angle diversion made of stainless steel, with stainless steel attachment to the standpipe - ball valve made of stainless steel as underfloor actuation, mounted in stainless steel cabinet, with pull rod activation 1000 mm, DIN-DVGW tested and certificated, with automatic self-draining in 1000 mm depth - base plate with 4 mounting holes of stainless steel, polished, dimensions 200 x 200 mm - stand pipe 1 ¼” of stainless steel three-part, polished, total height 2330 mm - wall shower arm ¾“ of stainless steel, polished, projection 600 mm - integrated automatic flow regulation 50 l/min. for a spray pattern acc. to the norms at a specified operating range of 1.5 to 3 bar dynamic water pressure - high-performance shower head of stainless steel, polished, with improved spray pattern, corrosion resistant, largely calcification- and maintenance-free, very robust, self-draining - sign for body safety shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 metre - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717 - according to ANSI Z358.1-2014, EN 15154-1:2006 and EN 15154-5:2019 - DIN-DVGW tested and certificated Manufacturer: B-SAFETY or equal Article-No.: BR 888 395 Technical Specifications Minimum flow pressure: 1.5 bar Operating pressure: 1.5 to 3 bar Flow rate: 50 l/min Water inlet: ¾” male Product overview BR 888 395: flow rate 50 l/min (hazard class I according to EN 15154-5:2019) BR 888 395 / 75L: flow rate 75 l/min / 20 GPM (hazard class II according to EN 15154-5:2019) BR 888 395 / 110L: flow rate 110 l/min (hazard class III according to EN 15154-5:2019) |  |