| BR 810 095 | PremiumLine freestanding frostprotected heated body safety shower |
| --- | --- |
| PremiumLine frostprotected heated body safety shower, floor mounted - base plate with 4 mounting holes of stainless steel , dimensions 200 x 200 mm - stand pipe 1 ¼” of stainless steel two-part, with bottom water inlet 1 ¼” female, total height 2300 mm - connection pipe 1 ¼” of stainless steel, length 75 mm - ball valve 1 ¼” of stainless steel, with pull rod actuation, DIN-DVGW tested and certificated - pull rod with ring handle of stainless steel, length 700 mm - wall shower arm 1 ¼” of stainless steel, polished, projection 600 mm - high-performance shower head of chemical resistant plastics, black, with improved spray pattern, corrosion resistant, largely calcification- and maintenance-free, very robust, self-draining - insulation made of mineral wool shape package, non-flammable, according to DIN 4102 - heating by self-regulating trace tape, output 10 W/m, electrical supply 230 V - 50 Hz - outdoor thermostat and power-saving-circuit (shutdown of trace tape at 11°C, switch on at 4°C) - outer casing of the shower made of screwed stainless steel housing, easy to dismantle for maintenance work, including green/white indicator strips for better visibility of the shower - sign for body safety shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 meter - suitable for use in EX-Zones 1 & 2, all electrical parts explosion-proof, with risk assessment in accordance with industrial safety regulations concerning the non-electrical and electrical explosion protection - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717 - according to ANSI Z358.1-2014, EN 15154-1:2006 and EN 15154-5:2019 - DIN-DVGW tested and certificated Manufacturer: B-SAFETY or equal Article-No.: BR 810 095 Technical Specifications Minimum flow pressure: 2 bar Operating pressure: 2 to 8 bar Flow rate: 50 l/min Water inlet: 1 ¼” male Electrical supply: 230 V - 50 Hz Product overview BR 810 095: flow rate 50 l/min (hazard class I according to EN 15154-5:2019) BR 810 095/ 110L: flow rate 110 l/min (hazard class III according to EN 15154-5:2019) |  |