| BR 718 020 | PremiumLine hand-held eye shower of stainless steel, with one spray head, table mounted |
| --- | --- |
| PremiumLine hand-held eye shower of stainless steel, with one spray head, table mounted - water-bearing parts made of stainless steel - handle with big, adjusting push lever made of stainless steel, polished, valve not self-closing - high-performance spray head made of stainless steel for large-scale dispersion of water, with plastic spray plate, largely free of calcification, with rubber sleeve and sealed dust cap - integrated flow regulation 7 litre / minute for a standard-compliant jet pattern at a specified working range of 1.5 to 5 bar flow pressure - integrated backflow preventer to protect the drinking water - stainless steel covered hose, length 1.5 meter, water inlet ½” female, DIN-DVGW tested and certificated - table mounting accessories M28x1,5x80mm made of stainless steel, incl. fastening-parts kit with nut M28x1,5mm and 2 screws M5 for mounting difficult to access, chrome-plated rosette, sealing to table surface with O-Ring - sign for eye shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 100 x 100 mm, viewing distance 10 metre - mounting height 770 mm (± 200 mm) - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717 - according to ANSI Z358.1-2014 and EN 15154-2:2006 - DIN-DVGW tested and certificated Manufacturer: B-SAFETY or equal Article-No.: BR 718 020 Technical Specifications Minimum flow pressure: 1.5 bar Operating pressure: 1.5 to 5 bar Flow rate: 7 l/min Water inlet: ½“ female Dimensions (H x W x D): 210 x 65 x 100 mm |  |