| BR 305 085 | ClassicLine safety eye shower with bowl, floor mounted |
| --- | --- |
| ClassicLine safety eye shower with bowl, floor mounted - base plate with 4 mounting holes of stainless steel, chemical resistant green powder coated, dimensions 200 x 200 mm - stand pipe 1 ¼” of stainless steel, chemical resistant green powder coated, with top and bottom water inlet 1 ¼” female, total height 1040 mm - connection pipe of stainless steel for easy installation and alignment of the shower, chemical resistant green powder coated - ball valve ½” of stainless steel, with PUSH-lever actuation, DIN-DVGW tested and certificated - push plate made of steel, chemical resistant green powder coated, length 240 mm, with large signal "PUSH", luminescent according to DIN 67510 - integrated flow regulation 14 litre / minute for a standard-compliant jet pattern at a specified working range of 2.5 to 5 bar flow pressure - high-performance spray heads for large-scale dispersion of water, with plastic spray plate, low calcification, incl. rubber sleeves and sealed dust caps, mounted over distributor fork - bowl made of plastic, green, diameter 275 mm, water outlet 1 ¼” male - sign for eye shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 100 x 100 mm, viewing distance 10 metre - total height 1040 mm, projection 425 mm, total width incl. lever 400 mm - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717 - according to ANSI Z358.1-2014 and EN 15154-2:2006 - DIN-DVGW tested and certificated Manufacturer: B-SAFETY or equal Article-No.: BR 305 085 Technical Specifications Minimum flow pressure: 2.5 bar Operating pressure: 2.5 to 5 bar Flow rate: 14 l/min Water inlet: 1 ¼” female Water outlet: 1 ¼” male |  |