| BR 852 085 | ClassicLine eye-/face wash unit with bowl and lid, floor mounted |
| --- | --- |
| ClassicLine eye-/face wash unit with bowl and lid, floor mounted - base plate with 4 mounting holes of stainless steel, chemical resistant green powder coated, dimensions 200 x 200 mm - stand pipe 1 ¼” of stainless steel, chemical resistant green powder coated, with top and bottom water inlet 1 ¼” female, total height 1025 mm - housing, lid and bowl made of UV and impact resistant ABS plastics, water outlet 1 ½“ male - integrated protective cover against dust - actuation by pulling down the lid - ball valve 3/8“ of brass, with lever actuation by lid, DIN-DVGW tested and certificated - aerators made of brass with a very limited spray pattern, chrome-plated - with integrated flow regulation valve 3/8” for setting the desired spray height and flow rate, water inlet 3/8” male - inclusive sign for eye shower according to DIN EN ISO 7010 und ASR A1.3 on the lid, dimensions 170 x 170 mm, viewing distance 17 metre - height 1025 mm, width 350 mm, depth 355 mm - mounting height (lower edge) 910 mm (± 200 mm) - according to BGI/GUV-I 850-0, DIN 1988 and DIN EN 1717 - according to ANSI Z358.1-2014 and DIN EN 15154-2:2006 - DIN-DVGW tested and certificated Manufacturer: B-SAFETY or equal Article-No.: BR 852 085 Technical Specifications Minimum flow pressure: 2.5 bar Operating pressure: 2.5 to 5 bar Flow rate: 14-20 l/min Water inlet: 1 ¼” female Water outlet: 1 ½” male |  |